## INTRO
List of sheets
# | name | name2 | comments
Building energy modelling
1 | Site |  | building main caracteristics
2 | Schedules
3 | Construction | whole building
4 |  | IGUs
5 | Loads
6 | Space types
7 | Facility
8 | Spaces |  | shading controls and frames caracteristics
9 | HVAC | HVAC classic VAV system
10 |  | HVAC optimised VAV system
11 |  | HVAC optimised VRF system
12 | Thermal zones |  | heating & cooling sizing parameters, see also hvac above
13 | Output variables
BEM and LCA simulations
14 | Simulations |  | define the scenarios and the scope of the sensitivity analysis
BEM and LCA simulations
15 | Hypotheses for the frames |  | more information in the LCI datasets (Excel files)
16 | Hypotheses for the igus |  | more information in the LCI datasets (Excel files)

## Site
Site
Weather Data
Brussels | energyplus.net/weather
Design Days
Summer DD | BRUSSELS Ann Clg .4% Condns DB=>MWB
Winter DD | BRUSSELS Ann Htg 99.6% Condns DB
References
ASHRAE 2009. Handbook of Fundamental, Chapter 14
> Which DD should we use?
Annual Heating and Humidification Design Conditions "The month with the lowest mean dry-bulb temperature is used, for example, to determine the time of year where the maximum heating load occurs. The 99.6 and 99.0% design conditions are often used in sizing heating equipment." Annual Cooling, Dehumidification, and Enthalpy Design Conditions. "[...] The 0.4, 1.0, and 2.0% dry-bulb temperatures and mean coincident wet-bulb temperatures often represent conditions on hot, mostly sunny days. These are often used in sizing cooling equipment such as chillers or air-conditioning units."
Cooling
DB=>MWB | Chillers and air conditionners
Condns WB=> MDB | Cooling Towers and other evaporative coolers
DP=>MDB | useful for humidity control applications, i.e. desiccant cooling and dehumidification, cooling-based dehumidification, and fresh-air ventilation systems
Condns Enth=>MDB | this is used for calculating cooling loads caused by infiltration and/or ventilation into buildings. Enthalpy represents the total heat content of air (the sum of its sensible and latent energies)
Heating
Condns DB | General heating applications
Condns DP=>MCDB | to size equipment for humidification applications.
Condns WS=>MCDB | Wind design data provide information for estimating peak loads accounting for infiltration
2013 Annual Design Conditions Definitions for all ASHRAE Design Condition Locations:
http://energyplus.helpserve.com/knowledgebase/article/View/129/47/design-conditions-definitions-annual-for-all-ashrae-2013-design-condition-locations

## Schedules
Schedules
Spaces | Type | References | Remarks | Units | Period | 0-1 | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10-11 | 11-12 | 12-13 | 13-14 | 14-15 | 15-16 | 16-17 | 17-18 | 18-19 | 19-20 | 20-21 | 21-22 | 22-23 | 23-24
Offices
| Equipments / Full | From DOE Prototype Buildings | - | - | weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Sundays/holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Equipments / 75% | From DOE Prototype Buildings | We consider that the relation btw occupancy/equipement is not linear. A 75% occupancy does not equal a 75% equipment use. Hyp: 80% | - | weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Sundays/holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Lights | ASHRAE Schedules, From DOE Prototype Buildings (decrease at the end slightly postponed, 1 hour, 6pm instead of 5 pm) | - | - | weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3 | 0.3 | 0.2 | 0.1 | 0.05
[5 empty] | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Sundays/holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Occupancy / Full | ASHRAE Schedules, adapted according to Obyn et al. | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
| Occupancy / 75% | ASHRAE Schedules, adapted according to Obyn et al. | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.7 | 0.7 | 0.7 | 0.7 | 0.35 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | ASHRAE Schedules, revised. Temperature values: ISO13790, 2008 in Obyn et al. | Temperature values change based on the sensitivity analysis. | °C | weekdays | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16
[5 empty] | Saturdays | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 16
[5 empty] | Sundays/holidays | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Cooling | ASHRAE Schedules, revised. Temperature values: ISO13790, 2008 in Obyn et al. | Temperature values change based on the sensitivity analysis. | °C | weekdays | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 29 | 29
[5 empty] | Saturdays | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29
[5 empty] | Sundays/holidays | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
| People activity | Obyn et al. | total heat (adapted men/women) for seated, very light work | W | Default | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
Hall and corridors
| Lights | ASHRAE Schedules | - | - | weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.3 | 0.1 | 0.05 | 0.05
[5 empty] | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Sundays/holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Elevators | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.7 | 0.45 | 0.4 | 0.45 | 0.6 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.2 | 0.1 | 0.05 | 0.05 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.2 | 0.2 | 0.25 | 0.2 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equipments | From DOE Prototype Buildings | - | - | weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Sundays/holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| People activity | Obyn et al. | total heat (adapted men/women) for slow walking or standing activity | W | Default | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
| Occupancy | See offices | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | ASHRAE Schedules, revised | - | °C | weekdays | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16
[5 empty] | Saturdays | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 16
[5 empty] | Sundays/holidays | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Data center
| Equipments | ASHRAE Schedules | - | - | weekdays | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
[5 empty] | Saturdays | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
[5 empty] | Sundays/holidays | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
| Lights | ASHRAE Schedules | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HVAC | - | - |  | Default | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Heating | - | - | °C | weekdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Saturdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Sundays/holidays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
| Cooling | - | - | °C | weekdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Saturdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Sundays/holidays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Basement
| Lights | - | - | - | weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Sundays/holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Occupancy | - | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.7 | 0.7 | 0.7 | 0.7 | 0.35 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HVAC | ASHRAE Schedules | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | ASHRAE Schedules |  |  | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  | ASHRAE Schedules |  |  | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration
| Infill Quarter On | ASHRAE Schedules | when system on, the infiltration is reduced to 0.25 of the full value because assume that when the system is on, the building is pressurized. When system off, assume that infiltration can move freely into the building. According to the National Institute of Standards and Technology (US), this isn't necessarily the case. They created this OS measure: https://bcl.nrel.gov/node/83101 | - | weekdays | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  | ASHRAE Schedules |  |  | Saturdays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  | ASHRAE Schedules |  |  | Sundays/holidays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC
| Chilled Water Temperature |  | "=44F, From AHRI standard test conditions, 44F Leaving water temperature (LWT), and 54F for EWT. For water cooling tower, Wet bulb temperature of outside air (EAT wb) (in standard conditions)= 78F; LWT: 85F; EWT: 95. i.e., range of 10F and an approach of 7F. This means a design to come close to 7F of this value. That gives 85F of chilled water temperature coming out. See: 2018 Standard for Performance Rating of Water-chilling and Heat Pump Water-heating Packages Using the Vapor Compression Cycle. http://www.ahrinet.org/App_Content/ahri/files/STANDARDS/AHRI/AHRI_Standard_551-591_SI_2018.pdf | °C | default | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
| Deck Temperature |  | Space temp =75F, deck =spacetemp - 20F = 55F > 24°C et 13°C. Idem pour l'hiver, même SAT car des locaux ont besoin de cooling même en hiver, le reste faisant (beaucoup trop) de reheat. VAV with reheat systems are usually controlled at the central air handling unit to a cool deck temperature (usually 55F),. supply air temperature; default value is 20F below space temperature for cooling (usually set at 75°F, 24°C) | °C | default | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| Deck Temperature |  | Space temp =75F, deck =spacetemp - 20F = 55F > 24°C et 13°C. Idem pour l'hiver, même SAT car des locaux ont besoin de cooling même en hiver, le reste faisant (beaucoup trop) de reheat. VAV with reheat systems are usually controlled at the central air handling unit to a cool deck temperature (usually 55F),. supply air temperature; default value is 20F below space temperature for cooling (usually set at 75°F, 24°C) | °C | default | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
| HVAC |  |  | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Construction
Construction
Roof
| _Roof | Built-up roofing | Roof insulation | Concrete floor, 200mm
Walls
structural wall, int | _Gypsum13_Concrete200mm_Gypsum13 | Gypsum 13mm | Concrete, 200mm | Gypsum 13mm
Floor and ceiling
Intermediate slab | _ConcreteAndCarpet | Carpet pad | Concrete, 200mm
ground contact surfaces, basement | _Concrete_300mm | Concrete, 300mm
Plenum | _DropCeiling | Ceiling
Materials
Thermal Curtain only | Brand | Isotiss | -
| Solar transmittance | 0.12 | -
| Solar reflectance | 0.71 | -
| Visible transmittance | 0.12 | -
| Visible Reflectance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
| Thermal transmittance | 0.05 | -
| Thickness | 0.01 | m
| Conductivity | 0.046 | W/m.K
| Shade to glass distance | 0.05 | m
| Airflow permeability | 0.1 | -
Thermal Curtain w/ air wall | Brand | Isotiss | -
| Solar transmittance | 0.12 | -
| Solar reflectance | 0.71 | -
| Visible transmittance | 0.12 | -
| Visible Reflectance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
| Thermal transmittance | 0.05 | -
| Thickness | 0.13 | m
| Conductivity | 0.28261 | W/m.K
| Shade to glass distance | 0.05 | m
| Airflow permeability | 0.1 | -
Frame, low efficiency | Brand | Generic | -
| Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 5.5 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Frame, high efficiency | Brand | Wicona, Wictec 50 | -
| Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 1.2 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Frame, low efficiency w/ thermal curtain | Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 1.5581 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Frame, high efficiency w/ thermal curtain | Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 0.7732 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Exterior shading | Brand | https://verosol.com/product/enviroscreen-g3-optimum/
| Solar transmittance | 0.05 | -
| Solar reflectance | 0.74 | -
| Visible transmittance | 0.04 | -
| Visible Reflectance | 0.9 | -
| Thermal hemispherical emissivity | 0.9 | -
| Thermal transmittance | 0 | -
| Thickness | 0.0005 | m
| Conductivity | 0.15 | W/m.K
| Shade to glass distance | 0.05 | m
| Airflow permeability | 0.1 | -
| Emissivity front | 0.68 | -
| Emissivity back | 0.282 | -
| TIR | 0.149 | -
| Permeability factor | 0.111 | -
_Spandrel_Equivalent | Thickness | 0.205 | m
Equivalent to: 1 layer of safety glass, 8mm; 50mm of air cavity; 120mm of XPS insulation | Conductivity | 0.081 | W/m.K
| Density | 536 | kg/m³
| Specific heat | 1085 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
_Wall_Concrete300mm | Thickness | 0.3 | m
| Conductivity | 1.4
| Density | 2100 | kg/m³
| Specific heat | 840 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Carpet pad | Thermal resistance | 0.22 | m².K/W
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Roof insulation | Thermal resistance | 5.31 | m².K/W
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Gypsum_13mm | Thickness | 0.0127 | m
| Conductivity | 0.16 | W/m.K
| Density | 800 | kg/m³
| Specific heat | 1090 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.5 | -
_Ceiling | Thickness | 0.02 | m
| Conductivity | 0.057 | W/m.K
| Density | 288 | kg/m³
| Specific heat | 1339 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.5 | -
_Floor_Concrete200mm | Thickness | 0.2 | m
| Conductivity | 1.4 | W/m.K
| Density | 2100 | kg/m³
| Specific heat | 840 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Std Wood | Thickness | 0.15 | m
| Conductivity | 0.12 | W/m.K
| Density | 540 | kg/m³
| Specific heat | 1210 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Bronze Glass_6mm | Thickness | 0.006 | m
Calculated with Window 7.7 software | Solar transmittance | 0.486 | -
| Front side solar reflectance | 0.053 | -
| Back side solar reflectance | 0.053 | -
| Visible Transmittance | 0.533 | -
| Front side visible reflectance | 0.056 | -
| Back side visible reflectance | 0.056 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 1 | W/m.K
Clear_55.2 | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.7 | -
| Front side solar reflectance | 0.066 | -
| Back side solar reflectance | 0.066 | -
| Visible Transmittance | 0.868 | -
| Front side visible reflectance | 0.078 | -
| Back side visible reflectance | 0.078 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 0.791 | W/m.K
Clear_55.2_HighLT_HighSHGC | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.753 | -
| Front side solar reflectance | 0.069 | -
| Back side solar reflectance | 0.069 | -
| Visible Transmittance | 0.879 | -
| Front side visible reflectance | 0.079 | -
| Back side visible reflectance | 0.079 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 0.787 | W/m.K
Clear 6mm | Thickness | 0.006 | m
Calculated with Window 7.7 software | Solar transmittance | 0.809 | -
| Front side solar reflectance | 0.072 | -
| Back side solar reflectance | 0.072 | -
| Visible Transmittance | 0.888 | -
| Front side visible reflectance | 0.079 | -
| Back side visible reflectance | 0.079 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 1 | W/m.K
Clear_6mm_HighLT | Thickness | 0.006 | m
Calculated with Window 7.7 software | Solar transmittance | 0.353 | -
| Front side solar reflectance | 0.375 | -
| Back side solar reflectance | 0.494 | -
| Visible Transmittance | 0.787 | -
| Front side visible reflectance | 0.081 | -
| Back side visible reflectance | 0.077 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.841 | -
| Conductivity | 1 | W/m.K
Clear 8mm | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.777 | -
| Front side solar reflectance | 0.07 | -
| Back side solar reflectance | 0.07 | -
| Visible Transmittance | 0.878 | -
| Front side visible reflectance | 0.078 | -
| Back side visible reflectance | 0.078 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 1 | W/m.K
LowE_55.2_HighLT | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.464 | -
| Front side solar reflectance | 0.394 | -
| Back side solar reflectance | 0.255 | -
| Visible Transmittance | 0.82 | -
| Front side visible reflectance | 0.084 | -
| Back side visible reflectance | 0.102 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.03 | -
| Back side infrared emissivity | 0.841 | -
| Conductivity | 0.787 | W/m.K
LowE_55.2_LowLT_LowSHGC | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.464 | -
| Front side solar reflectance | 0.082 | -
| Back side solar reflectance | 0.089 | -
| Visible Transmittance | 0.679 | -
| Front side visible reflectance | 0.078 | -
| Back side visible reflectance | 0.075 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 0.865 | W/m.K
SC_8mm_HighLT_HighSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.353 | -
| Front side solar reflectance | 0.375 | -
| Back side solar reflectance | 0.494 | -
| Visible Transmittance | 0.787 | -
| Front side visible reflectance | 0.081 | -
| Back side visible reflectance | 0.077 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.031 | -
| Conductivity | 1 | W/m.K
SC_8mm_LowLT_LowSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.27 | -
| Front side solar reflectance | 0.314 | -
| Back side solar reflectance | 0.5 | -
| Visible Transmittance | 0.539 | -
| Front side visible reflectance | 0.147 | -
| Back side visible reflectance | 0.163 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.028 | -
| Conductivity | 1 | W/m.K
SC_8mm_LowLT_VeryLowSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.187 | -
| Front side solar reflectance | 0.38 | -
| Back side solar reflectance | 0.619 | -
| Visible Transmittance | 0.386 | -
| Front side visible reflectance | 0.297 | -
| Back side visible reflectance | 0.313 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.028 | -
| Conductivity | 1 | W/m.K
SC_8mm_midLT_midSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.243 | -
| Front side solar reflectance | 0.365 | -
| Back side solar reflectance | 0.489 | -
| Visible Transmittance | 0.557 | -
| Front side visible reflectance | 0.116 | -
| Back side visible reflectance | 0.075 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.025 | -
| Conductivity | 1 | W/m.K
SC_8mm_midLT_midSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.243 | -
| Front side solar reflectance | 0.365 | -
| Back side solar reflectance | 0.489 | -
| Visible Transmittance | 0.557 | -
| Front side visible reflectance | 0.116 | -
| Back side visible reflectance | 0.075 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.025 | -
| Conductivity | 1 | W/m.K

## Construction_igus
| Construction, glazing | [8 empty] | Data Window7.7
[14 empty] | U-Factor | SHGC | VT |  |  |  | Data Window7.7
| Name part 1 | Information |  | U-Factor | SHGC | VT | Name part 2 | Name part 3 |  |  | 1 | 2 | 3 | W/m².K | - | -
# |  | Brand | Gas | W/m².K | - | - |  |  | ref | DG_8-10-55.2_bronze | Planibel Bronze | Stratobel Clearlite | - | 2.706 | 0.464 | 0.364 |  |  |  |  | Tsol | Rsol | Tvis
| Single Glazing | [18 empty] | 55.2
sg_1 | SG_55.2_clear | Stratobel Clearlite |  | 5.57 | 0.808 | 0.879 | - | - | 1 | DG_8-10-55.2_clear | Clear | Stratobel Clearlite | - | 2.706 | 0.692 | 0.768 |  |  | 4509 | Stratobel Clearlite | 0.753 | 0.069 | 0.879
sg_2 | SG_¦55.2_clear | Stratobel iplus Top 1.0 |  | 3.099 | 0.445 | 0.745 | - | - | [10 empty] | 4430 | Stratobel Low-e Top N+ | 0.492 | 0.18 | 0.84
[9 empty] | 1 | SG_55.2_clear | Stratobel Clearlite | - | - | 5.57 | 0.808 | 0.879 |  |  | 4253 | Stratobel iplus Top 1.0 | 0.391 | 0.274 | 0.745
| Double Glazing Old | [7 empty] | 2 | SG_¦55.2_clear | Stratobel iplus Top 1.0 | - | - | 3.099 | 0.445 | 0.745
dg_init | DG_8-10-55.2_bronze | Planibel Bronze + Stratobel Clearlite |  | 2.706 | 0.464 | 0.364 | - | - | [11 empty] | 8mm
dg_0 | DG_8-10-55.2_clear | Clear + Stratobel Clearlite |  | 2.706 | 0.692 | 0.768 | - | - | 1 | DG_8-18Arg-55.2_clear | Clearvision | Stratobel Clearlite | - | 2.51 | 0.785 | 0.806 |  |  | 891 | Clear | 0.761 | 0.067 | 0.869
[9 empty] | 2 | DG_8-18Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | - | 1.435 | 0.592 | 0.768 | highSHG_highLT |  | 4336 | Clearvision | 0.892 | 0.078 | 0.911
| Double Glazing High Efficiency | [7 empty] | 3 | DG_8-18Arg-¦55.2_ | Clearvision | Stratobel iplus Top 1.0 | - | 1.419 | 0.481 | 0.687 |  |  | 4370 | Planibel top Nplus | 0.572 | 0.284 | 0.86
dg_1 | DG_8-18Arg-¦55.2 | AGC, Iplus Advanced 1.0T on Clearlite | 90% argon | 1.1 | 0.62 | 0.82 | highSHG_highLT | - | 4 | DG_8¦-18Arg-55.2_ | Planibel top Nplus | Stratobel Clearlite | - | 1.45 | 0.539 | 0.76 | midSHG_highLT |  | 4446 | Stopray Vision-36T | 0.187 | 0.619 | 0.386
dg_2 | DG_8¦-18Arg-55.2 | AGC, Sunergy | 90% argon | 1 | 0.41 | 0.58 | midSHG_midLT | - | 5 | DG_8¦-18Arg-¦55.2_ | Planibel top Nplus | Stratobel Low-e Top N+ | - | 1.404 | 0.482 | 0.725 |  |  | 4211 | Sunergy Clear | 0.498 | 0.104 | 0.669
dg_3 | DG_8¦-18Arg-55.2 | AGC, Iplus Energy on Clearlite | 90% argon | 1.1 | 0.41 | 0.74 | midSHG_highLT | - | 6 | DG_8¦-18Arg-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | - | 1.398 | 0.408 | 0.647 |  |  | 4239 | Stopsol Classic Clear | 0.473 | 0.277 | 0.374
dg_4 | DG_8¦-18Arg-¦55.2 | AGC, Stopray Vision-72 | 90% argon | 1 | 0.21 | 0.4 | lowSHG_lowLT | - | 7 | DG_8¦-18Arg-55.2_ | Stopray Vision-36T | Stratobel Clearlite | - | 1.424 | 0.203 | 0.348 |  |  | 4478 | Stopray Vision-72 | 0.353 | 0.494 | 0.787
dg_5 | DG_8¦-18Arg-55.2 | AGC, Stopray ipasol ultraselect 62/29 | 90% argon | 1 | 0.29 | 0.62 | lowSHG_midLT | - | 8 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-36T | Stratobel Low-e Top N+ | - | 1.397 | 0.198 | 0.33 |  |  | 4469 | Stopray Vision-51T | 0.243 | 0.489 | 0.557
dg_6 | DG_8¦-18Arg-55.2 | AGC, Stopray Ultra-60 | 90% argon | 1 | 0.38 | 0.72 | lowSHG_highLT | - | 9 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | - | 1.393 | 0.183 | 0.302 | lowSHG_lowLT
[9 empty] | 10 | DG_8¦-18Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | - | 1.405 | 0.248 | 0.493 | lowSHG_midLT |  |  | 6mm
| Triple Glazing | [7 empty] | 11 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | - | 1.39 | 0.244 | 0.47 |  |  | 4340 | Planibel Clearvision | 0.637 | 0.118 | 0.789
tg_1 | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, iplus Top 1.1 on Clearlite | 90% argon | 0.6 | 0.54 | 0.75 | highSHG_highLT | - | 12 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel iplus Top 1.0 | - | 1.387 | 0.22 | 0.421
tg_2 | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, Planibel top Nplus | 90% argon | 0.7 | 0.37 | 0.52 | midSHG_midLT | - | 13 | DG_8¦-18Arg-55.2_ | Sunergy Clear | Stratobel Clearlite | - | 1.903 | 0.492 | 0.593 | midSHG_midLT |  |  | 8mm, bronze
tg_3 | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, ipasol neutral 70/39 | 90% argon | 0.7 | 0.35 | 0.64 | midSHG_highLT | - | 14 | DG_8¦-18Arg-¦55.2_ | Sunergy Clear | Stratobel Low-e Top N+ | - | 1.43 | 0.403 | 0.565 |  |  | 4456 | Sunlux Orion Bronze | 0.179 | 0.13 | 0.18
tg_4 | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, Stopray Vision-36T | 90% argon | 0.6 | 0.19 | 0.33 | lowSHG_lowLT | - | 15 | DG_8¦-18Arg-¦55.2_ | Sunergy Clear | Stratobel iplus Top 1.0 | - | 1.416 | 0.341 | 0.507 |  |  | 4268 | Planibel Bronze | 0.431 | 0.051 | 0.413
tg_5 | TG_8¦-14Arg-6-14Arg-55.2 | AGC, Stopray Ultra-50 on Clearvision | 90% argon | 0.6 | 0.21 | 0.46 | lowSHG_midLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
tg_6 | TG_8¦-14Arg-6-14Arg-55.2 | AGC, ipasol neutral | 90% argon | 0.6 | 0.34 | 0.64 | lowSHG_highLT | - | 17 | DG_8¦-18Arg-¦55.2_ | Stopsol Classic Clear | Stratobel Low-e Top N+ | - | 1.435 | 0.31 | 0.32
| Double Glazing, w/ krypton and xenon | [7 empty] | 11 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | - | 1.39 | 0.244 | 0.47 |  |  | 4340 | Planibel Clearvision | 0.637 | 0.118 | 0.789
dg_5k | DG_8¦-18Krypton-55.2 | AGC, Stopray ipasol ultraselect 62/29 | 90% krypton | 0.7 | 0.29 | 0.62 | lowSHG_midLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
[9 empty] | 18 | DG_8¦-18Arg-¦55.2_ | Stopsol Classic Clear | Stratobel iplus Top 1.0 | - | 1.419 | 0.256 | 0.293
| Triple Glazing, w/ krypton and xenon | [7 empty] | 11 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | - | 1.39 | 0.244 | 0.47 |  |  | 4340 | Planibel Clearvision | 0.637 | 0.118 | 0.789
tg_5k | TG_8¦-14Krypton-6-14Krypton-55.2 | AGC, Stopray Ultra-50 on Clearvision | 90% krypton | 0.5 | 0.21 | 0.46 | lowSHG_midLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
tg_5x | TG_8¦-14Xenon-6-14Xenon-55.2 | AGC, Stopray Ultra-50 on Clearvision | 90% xenon | 0.45 | 0.21 | 0.46 | lowSHG_midLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
[9 empty] | 18 | DG_8¦-18Arg-¦55.2_ | Stopsol Classic Clear | Stratobel iplus Top 1.0 | - | 1.419 | 0.256 | 0.293
| Closed Cavity Facade | [7 empty] | 19 | DG_8¦-18Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | - | 1.43 | 0.341 | 0.696 | lowSHG_highLT
ccf | SG_¦55.2_clear + 20cm + DG_8¦-18Arg-55.2 |  |  | 0.75 | 0.2 | 0.44 |  |  | 20 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel Low-e Top N+ | - | 1.399 | 0.335 | 0.664
[9 empty] | 21 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel iplus Top 1.0 | - | 1.394 | 0.3 | 0.594
| Vacuum double glazing | [7 empty] | 19 | DG_8¦-18Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | - | 1.43 | 0.341 | 0.696 | lowSHG_highLT
dg_smart | Vacuum glazing 8-vacuum-55.2 |  |  | 0.6 | 0.29 | 0.62 |  |  | 20 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel Low-e Top N+ | - | 1.399 | 0.335 | 0.664
[9 empty] | 21 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel iplus Top 1.0 | - | 1.394 | 0.3 | 0.594
| Smart Glazing | [7 empty] | 19 | DG_8¦-18Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | - | 1.43 | 0.341 | 0.696 | lowSHG_highLT
dg_smart | Sage Glass, Saint Gobain | [7 empty] | 20 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel Low-e Top N+ | - | 1.399 | 0.335 | 0.664
[9 empty] | 21 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel iplus Top 1.0 | - | 1.394 | 0.3 | 0.594
[9 empty] | 1 | TG_8-14Arg-6-14Arg-55.2_clear | Clearvision | Stratobel Clearlite | Planibel Clearvision | 1.575 | 0.738 | 0.745
[9 empty] | 2 | TG_8-14Arg-6-14Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | Planibel Clearvision | 0.98 | 0.554 | 0.709 | highSHG_highLT
[9 empty] | 3 | TG_8-14Arg-6-14Arg-¦55.2_ | Clearvision | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.97 | 0.455 | 0.638
[9 empty] | 4 | TG_8¦-14Arg-6-14Arg-55.2_ | Planibel top Nplus | Stratobel Clearlite | Planibel Clearvision | 1.048 | 0.503 | 0.701
[9 empty] | 5 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Planibel top Nplus | Stratobel Low-e Top N+ | Planibel Clearvision | 0.689 | 0.451 | 0.668
[9 empty] | 6 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.682 | 0.386 | 0.6 | midSHG_highLT
[9 empty] | 7 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-36T | Stratobel Clearlite | Planibel Clearvision | 1.033 | 0.188 | 0.327
[9 empty] | 8 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-36T | Stratobel Low-e Top N+ | Planibel Clearvision | 0.681 | 0.178 | 0.31
[9 empty] | 9 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.674 | 0.164 | 0.284 | lowSHG_lowLT
[9 empty] | 10 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | Planibel Clearvision | 1.022 | 0.229 | 0.455 | lowSHG_midLT
[9 empty] | 11 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | Planibel Clearvision | 0.674 | 0.22 | 0.434
[9 empty] | 12 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-51T | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.667 | 0.199 | 0.39
[9 empty] | 13 | TG_8¦-14Arg-6-14Arg-55.2_ | Sunergy Clear | Stratobel Clearlite | Planibel Clearvision | 1.293 | 0.453 | 0.549
[9 empty] | 14 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Sunergy Clear | Stratobel Low-e Top N+ | Planibel Clearvision | 0.828 | 0.374 | 0.523 | midSHG_midLT
[9 empty] | 15 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Sunergy Clear | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.819 | 0.318 | 0.471
[9 empty] | 16 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | Planibel Clearvision | 1.574 | 0.434 | 0.318
[9 empty] | 17 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopsol Classic Clear | Stratobel Low-e Top N+ | Planibel Clearvision | 0.979 | 0.293 | 0.301
[9 empty] | 18 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopsol Classic Clear | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.969 | 0.244 | 0.276
[9 empty] | 19 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | Planibel Clearvision | 1.037 | 0.318 | 0.643 | lowSHG_highLT
[9 empty] | 20 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-72 | Stratobel Low-e Top N+ | Planibel Clearvision | 0.822 | 0.303 | 0.614
[9 empty] | 21 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-72 | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.819 | 0.275 | 0.553
Single Glazing w/ thermal curtain
[9 empty] | 1AT | SG_55.2_clear | Stratobel Clearlite | 0 | #REF! | 1.5636 | 0.808 | 0.879 | - | _TC
[9 empty] | 1BT | SG_¦55.2_clear | Stratobel iplus Top 1.0 | 0 | #REF! | 1.2777 | 0.445 | 0.745 | - | _TC
Double Glazing Old w/ thermal curtain
[9 empty] | 0AT | DG_8-10-55.2_bronze | Planibel Bronze + Stratobel Clearlite | 0 | #REF! | 1.2055 | 0.464 | 0.364 | - | _TC
[9 empty] | 0BT | DG_8-10-55.2_clear | Clear + Stratobel Clearlite | 0 | #REF! | 1.2055 | 0.692 | 0.768 | - | _TC
Double Glazing w/ thermal curtain
[9 empty] | 2AT | DG_8¦-18Arg-¦55.2 | AGC, Stopray Vision-72 | 90% argon | #REF! | 0.68493 | 0.21 | 0.4 | lowSHG_lowLT | _TC
[9 empty] | 2BT | DG_8¦-18Arg-55.2 | AGC, Stopray Ultra-60 | 90% argon | #REF! | 0.68493 | 0.38 | 0.72 | lowSHG_highLT | _TC
[9 empty] | 2CT | DG_8¦-18Arg-55.2 | AGC, Stopray ipasol ultraselect 62/29 | 90% argon | #REF! | 0.68493 | 0.29 | 0.62 | lowSHG_midLT | _TC
[9 empty] | 2DT | DG_8-18Arg-¦55.2 | AGC, Iplus Advanced 1.0T on Clearlite | 90% argon | #REF! | 0.73041 | 0.62 | 0.82 | highSHG_highLT | _TC
[9 empty] | 2ET | DG_8¦-18Arg-55.2 | AGC, Iplus Energy on Clearlite | 90% argon | #REF! | 0.73041 | 0.41 | 0.74 | midSHG_highLT | _TC
[9 empty] | 2FT | DG_8¦-18Arg-55.2 | AGC, Sunergy | 90% argon | #REF! | 0.68493 | 0.41 | 0.58 | midSHG_midLT | _TC
Triple Glazing w/ thermal curtain
[9 empty] | 3AT | TG_8¦-14Arg-6-14Arg-55.2 | AGC, ipasol neutral | 90% argon | #REF! | 0.47022 | 0.34 | 0.64 | lowSHG_highLT | _TC
[9 empty] | 3BT | TG_8¦-14Arg-6-14Arg-55.2 | AGC, Stopray Ultra-50 on Clearvision | 90% argon | #REF! | 0.47022 | 0.21 | 0.46 | lowSHG_midLT | _TC
[9 empty] | 3CT | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, iplus Top 1.1 on Clearlite | 90% argon | #REF! | 0.47022 | 0.54 | 0.75 | highSHG_highLT | _TC
[9 empty] | 3DT | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, Planibel top Nplus | 90% argon | #REF! | 0.5295 | 0.37 | 0.52 | midSHG_midLT | _TC
[9 empty] | 3ET | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, ipasol neutral 70/39 | 90% argon | #REF! | 0.5295 | 0.35 | 0.64 | midSHG_highLT | _TC
[9 empty] | 3FT | TG_8¦-14Arg-6-14Arg-¦55.2 | AGC, Stopray Vision-36T | 90% argon | #REF! | 0.47022 | 0.19 | 0.33 | lowSHG_lowLT | _TC

## Loads
Loads
People
Basement_Density | per floor area | 0 | p/m²
Core_Density | floor area per pers | 2 | m²/p
| fraction radiant | 0.3 | -
Data Center_Density | per floor area | 0 | p/m²
Offices_Density | floor area per pers | 8-12 | m²/p | Open space, NBN-EN-13779, 2007, in Obyn et al.
| fraction radiant | 0.3 | - | > Flex office, plus de densité
Light
Offices_Recessed ligting | W per floor area | 5-10 | W/m² | /100 lux = 1-2 W/m². 500 lux for the office space > 8 à 10W/m², but could reach 5 W/m²
Recessed ligting, lighting (relatively low light level) via recessed ceiling luminaires supplemented by desk lamps. The internal load is reduced by the air return through the luminaires. | Fraction radiant | 0.37 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
Core_Recessed ligting | W per floor area | 3-6 | W/m²
| Fraction radiant | 0.37 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
Basement_Suspended lighting | W per floor area | 3 | W/m²
| Fraction radiant | 0.42 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
DataCenter_Recessed ligting | W per floor area | 0 | W/m²
| Fraction radiant | 0.37 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
Equipment
Office_Equipments_Plugs | W per floor area | 150 | W/pers | computer with charger, compact printer… (computer = 100-120 /pers
| Fraction latent | 0 | -
| Fraction radiant | 0.22 | - | https://help.iesve.com/ve2018/table_11_radiant_fraction_for_casual_gains.htm#
| Fraction lost | 0 | -
DataCenter_Plugs | W per floor area | 200 | W/m²
| Fraction latent | 0 | -
| Fraction radiant | 0.5 | -
| Fraction lost | 0 | -
Core_Equipments_Plug | W per floor area | 2 | W/m² | plusieurs/
| Fraction latent | 0 | -
| Fraction radiant | 0.5 | -
| Fraction lost | 0 | -
Core_Equipments_Elevators | Design level | 80 | W | ASHRAE 90.1-2010LobbyFor Elevator
| Fraction latent | 0 | -
| Fraction radiant | 0.5 | -
| Fraction lost | 0 | -
Basement_Equipments | W per floor area | 0 | W/m²
| Fraction latent |  | -
| Fraction radiant |  | -
| Fraction lost |  | -
Internal mass
Offices | Surface area | 4 | m²/p
| Construction | Wood furniture
Core | Surface area | 10 | m²
| Construction | Wood furniture

## Space types
Space types
Design specification outdoor air
Offices | Outdoor air flow per person | 0.0061111 | m³/s.p | https://www.cstc.be/homepage/index.cfm?cat=publications&sub=infofiches&pag=42&art=2&lang=fr#3
Core | Outdoor air flow per floor area | 0.00072222 | m³/s.p
Data center | Outdoor air flow per floor area | 0.000254 | m/s | ASHRAE 62.1-2007, Office Buildings, Telephone/data entry
Basement | Outdoor air flow per floor area | 0.00031 | m/s
Space Infiltration Design Flow Rates
Offices | Calculation method | Flow/Exterior Area
| Flow per Exterior Surface Area | 0.0003 | m/s

## Facility
Facility
Data
Number of stories | 10
Number of above ground stories | 9
Nominal floor to floor height | 3.7
Nominal floor to ceiling height | 3

## Spaces
Spaces
Shading controls
Exterior shade | Shading device material name | EnviroScreen 810/936, greylight)silver
| Shading control type | On if high zone air temp and high solar on window
| Schedule name | Exterior shading_on
| Setpoint 1 | 22 | °C
| Shading control is scheduled | Yes | -
| Glare control is active | Yes
| Setpoint 2 | 250 | W/m²
| Multiple surface control type | Sequential
Thermal curtain | Shading device material name | Int_Isotiss_Thermal Curtain and Air Wall
| Shading control type | On night if low outddor temp and off day
| Schedule name | Thermal curtain_on
| Setpoint 1 | 19 | °C
| Shading control is scheduled | Yes | -
| Glare control is active | No
Frame and divider |  | Brand | Wicona, Wictec 50
Frame, low efficiency | Frame width | 0.1 | m
Frame_LowPerf | Frame outside projection | 0.024 | m
| Frame inside projection | 0.12 | m
| Frame conductance | 5.5 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1
| Frame solar absorptance | 0.7
| Frame visible absorptance | 0.7
| Frame thermal hemispherical emissivity | 0.9
Frame, high efficiency | Frame width | 0.1 | m
Frame_HighPerf | Frame outside projection | 0.024 | m
| Frame inside projection | 0.12 | m
| Frame conductance | 1.5 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1
| Frame solar absorptance | 0.7
| Frame visible absorptance | 0.7
| Frame thermal hemispherical emissivity | 0.9
Frame, low efficiency, with thermal curtain | Frame width | 0.1 | m
Frame_LowPerf_TC | Frame outside projection | 0.024 | m
| Frame inside projection | 0.12 | m
| Frame conductance | 1.56 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1
| Frame solar absorptance | 0.7
| Frame visible absorptance | 0.7
| Frame thermal hemispherical emissivity | 0.9
Frame, high efficiency, with thermal curtain | Frame width | 0.1 | m
Frame_HighPerf_TC | Frame outside projection | 0.024 | m
| Frame inside projection | 0.12 | m
| Frame conductance | 1 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1
| Frame solar absorptance | 0.7
| Frame visible absorptance | 0.7
| Frame thermal hemispherical emissivity | 0.9

## hvac_init
HVAC systems, initial: dedicated outdoor air system (DOAS) with fan coil chiller with boiler
Two DOAS | open plan offices, core, hall, 15 zones
data centers, 3 zones
DOAS for open plan offices, core, hall |  |  |  |  | > | > | > | Systems
| Cooling type | chilled water
| Heating type | hot water
Time of operation | HVAC operation schedule | HVAC_Operation |  | see schedules
| Use night cycle | Cycle on full system if heating or cooling required | [5 empty] | - | ASHP | Air source heat pump
[11 empty] | definition | absorbs heat from a colder place and release it into a warmer place using the same vapor-compression refrigeration process and same external heat exchanger with fan as used by an air conditioners. Unlike an air conditioning unit, however, it is able to both warm and cool building
Supply air temperature | Supply air temperature schedule | controlled by an outdoor air rest setpoint manager
[8 empty] | x | EAHP | Exhaust Air Heat Pump
Mechanical ventilation | Economizer | no economizer | [8 empty] | definition | extracts heat from the exhaust air of a building and transfers the heat to the supply air, hot tap water and/or hydronic heating system (underfloor heating, radiators).
| Demand controlled ventilation | on
[8 empty] | x | GSHP | ground source heat pump
Availability managers | Applicability schedule | always on discrete |  | https://bigladdersoftware.com/epx/docs/8-9/input-output-reference/group-system-availability-managers.html
| Control type | Cycle on any | [5 empty] | v | VRF | Variable Refrigerant Flow
| Thermostat tolerance | 1 | K | [7 empty] | definition | use refrigerant as the cooling and heating medium. This refrigerant is conditioned by a single or multiple condensing units (which may be outdoors or indoors, water or air cooled), and is circulated within the building to multiple indoor units.
| Cycling run time control type | fixed run time
| Cycling run time | 3600 | s
Air loop | Design supply air flow rate | autosized | m³/s
| Design return air flow fraction of supply air flow | 1
Sizing system | Type of load to size on | Ventilation Requirement
| Design outdoor air flow rate | autosized
| Central heating maximum system air flow ratio | 1
| Preheat design temperature | 7 | °C
| Preheat design humidity ratio | 0.008 | kgH2O/kgair
| Precool design temperature | 12.8 | °C
| Precool design humidity ratio | 0.008 | kgH2O/kgair
| Central cooling design supply air temperature | 15.5 | °C
| Central heating design supply air temperature | 21 | °C
| Sizing option | coincident
| 100% outdoor air in cooling | yes
| 100% outdoor air in heating | yes
| Central cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Central heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | design day
| Cooling design air flow rate | 0 | m³/s
| Heating design air flow method | design day
| Heating design air flow rate | 0 | m³/s
| System outdoor air method | zone sum
| Zone maximum outdoor air fraction | 1
| Cooling Supply Air Flow Rate Per Floor Area | 0.01 | m/s
| Cooling Fraction of Authosized Cooling Supply Air Flow Rate | 1
| Cooling Supply Air Flow Rate Per Unit Cooling Capacity | 4e-05 | 1/Pa
| Heating Supply Air Flow Rate Per Floor Area | 0.01 | m/s
| Heating Fraction of Authorized Cooling Supply Air Flow Rate | 1
| Heating Fraction of Authorized Heating Supply Air Flow Rate | 1
| Heating Supply Air Flow Rate Per Unit Cooling Capacity | 3e-05 | 1/Pa
| Cooling Design Capacity Method | CoolingDesignCapacity
| Cooling Design Capacity | Autosized
| Cooling Design Capacity Per Floor Area | 234.7 | W/m²
| Fraction of Autosized Cooling Design Capacity | 1
| Heating Design Capacity Method | CoolingDesignCapacity
| Heating Design Capacity | Autosized
| Heating Design Capacity Per Floor Area | 157 | W/m²
| Fraction of Autosized Cooling Design Capacity | 1
| Central Cooling Capacity Control Method | OnOff
Coil heating water | Availability schedule name | Always on, discret | -
| U-factor times area value | autosized | W/K
| Maximum water flow rate | autosized | m³/s
| Performance input method | Ufactor times area and design water flow rate | -
| Rated capacity | autosized | W/K
| Rated inlet water temperature | 50 | °C
| Rated inlet air temperature | 16.5 | °C
| Rated outlet water temperature | 38 | °C
| Rated outlet air temperature | 32 | °C
| Rated ratio for air and water convection | 0.5 | -
Coil cooling water | Availability schedule name | Always on, discret
| Design water flow rate | autosized | m³/s
| Design inlet water temperature | autosized | °C
| Design inlet air temperature | autosized | °C
| Design outlet air temperature | autosized | °C
| Design inlet air humidity ratio | autosized | kgH2O/kgair
| Design outlet humidity ratio | autosized | kgH2O/kgair
| Type of analysis | simple analysis
| Heat exchanger configuration | cross flow
Fan Constant Volume | Fan total efficiency | 0.6 | -
| Pressure rise | 650 | Pa
| Maximum flow rate | autosized | m³/s
| Motor efficiency | 0.92
| Motor in Airstream fraction | 1 | -
Setpoint manager, outdoor air reset | Control variable | Temperature | -
| Setpoint at outdoor low temperature | 21 | °C
| Outdoor low temperature | 13 | °C
| Setpoint at outdoor high temperature | 15.5 | °C
| Outdoor high temperature | 21 | °C
Air Terminal Single Duct, Constant Volume, No Reheat
| Maximum air flow rate | autosized | m³/s
Thermal zones sizing: core, offices & hall | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Zone heating sizing factor |  | -
| Zone cooling sizing factor |  | -
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | 15.5 | -
| Dedicated outdoor air high setpoint temperature for design | 21 | -
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -
Chilled water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 40 | °C
| Minimum loop temperature | 1 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 6.7 | °C
| Loop design temperature difference | 5.6 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Chiller electric, EIR | Reference capacity | autosized | W
| Reference COP | 4.9 | -
| Reference leaving chilled water temperature | 6.7 | °C
| Reference entering condenser fluid temperature | 35 | °C
| Reference chilled water flow rate | autosized | m³/s
| Reference condenser fluid flow rate | autosied | m³/s
| Minimum part load ratio | 0.15 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Minimum unloading ratio | 0.25 | -
| Condenser fan power ratio | 0 | -
| Fraction of compressor electric consumption rejected by condenser | 1 | -
| Leavind chilled water lower temperature limit | 2.2 | °C
| Chiller flow mode | constant flow
Heat exchanger, fluid to fluid | Loop demand side design flow rate | autosized | m³/s
| Loop supply side design flow rate | autosized | m³/s
| Heat exchange mode type | counter flow
| Heat exchanger U-factor times area value | autosized | W/K
| Control type | cooling differential on/off
| Minimum temperature difference to activate heat exchanger | 0 | K
| Heat transfer metering end use type | free cooling
| Operation minimum temperature limit | 1.7 | °C
| Operation maximum temperature limit | 22 | °C
Hot water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 10 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 49 | °C
| Loop design temperature difference | 11 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Boiler hot water | Fuel type | Natural gas | -
| Nominal capacity | autosized | W
| Nominal thermal efficiency | 0.93 | -
| Efficiency curve temperature evaluation variable | Leaving boiler | -
| Design water flow rate | autosized | -
| Minimum part load ratio | 0 | -
| Maximum part load ratio | 1.2 | -
| Optimum part load ratio | 1 | -
| Water outlet upper temperature limit | 95 | °C
| Boiler flow mode | Leaving setpoint modulated | -
| Parasitic electric load | 0 | W
| Sizing factor | 1
Condenser water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 80 | °C
| Minimum loop temperature | 5 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 29.5 | °C
| Loop design temperature difference | 5.5 | K
| Sizing option | coincident
| Zone timesteps in averaging window | 1
Cooling tower, variable speed | Design inlet air wet-bulb temperature | 25.5 | °C
| Design approach temperature | 4 | K
| Design range temperature | 5.5 | K
| Design water flow rate | autosized | -
| Design air flow rate | autosized | -
| Design fan power | 45735 | W
| Minimum air flow rate ratio | 0.2 | -
| Fraction of tower capacity in free convection regime | 0.125 | -

## hvac_VAV
HVAC system: Variable Air Volume (VAV) chiller with gas boiler reheat
Two VAV systems | open plan offices, core, hall, 15 zones
data centers, 3 zones
VAV with reheat |  |  |  |  | > | > | > | Systems
| Cooling type | chilled water
| Heating type | hot water
Time of operation | HVAC operation schedule | HVAC_Operation |  | see schedules | 15 Zone VA
| Use night cycle | Cycle on full system if heating or cooling required | [5 empty] | - | ASHP | Air source heat pump
[11 empty] | definition | absorbs heat from a colder place and release it into a warmer place using the same vapor-compression refrigeration process and same external heat exchanger with fan as used by an air conditioners. Unlike an air conditioning unit, however, it is able to both warm and cool building
Supply air temperature | Supply air temperature schedule | deck temperature |  | see schedule
[8 empty] | x | EAHP | Exhaust Air Heat Pump
Mechanical ventilation | Economizer | no economizer | [8 empty] | definition | extracts heat from the exhaust air of a building and transfers the heat to the supply air, hot tap water and/or hydronic heating system (underfloor heating, radiators).
| Demand controlled ventilation | off
[8 empty] | x | GSHP | ground source heat pump
Availability managers | Name | Night cycle 1 |  | https://bigladdersoftware.com/epx/docs/8-9/input-output-reference/group-system-availability-managers.html | [6 empty] | definition | heat pump used to heat and/or cool a building by exchanging heat with ground, often through a vapor-compression refrigeration cycle. It uses the earth all the time, without any intermittency, as a heat source (in the winter) or a heat sink (in the summer).
| Applicability schedule | always on discrete
| Control type | Cycle on any | [5 empty] | v | VRF | Variable Refrigerant Flow
| Thermostat tolerance | 1 | K | [7 empty] | definition | use refrigerant as the cooling and heating medium. This refrigerant is conditioned by a single or multiple condensing units (which may be outdoors or indoors, water or air cooled), and is circulated within the building to multiple indoor units.
| Cycling run time control type | fixed run time
| Cycling run time | 1800 | s
Air loop | Design supply air flow rate | autosized | m³/s
| Design return air flow fraction of supply air flow | 1
Sizing system | Type of load to size on | sensible
| Design outdoor air flow rate | autosized
| Central heating maximum system air flow ratio | 0.3
| Preheat design temperature | 7 | °C
| Preheat design humidity ratio | 0.008 | kgH2O/kgair
| Precool design temperature | 12.8 | °C
| Precool design humidity ratio | 0.008 | kgH2O/kgair
| Central cooling design supply air temperature | 12.8 | °C
| Central heating design supply air temperature | 12.8 | °C
| Sizing option | Coincident
| 100% outdoor air in cooling | No
| 100% outdoor air in heating | No
| Central cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Central heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | design day
| Cooling design air flow rate | 0 | m³/s
| Heating design air flow method | design day
| Heating design air flow rate | 0 | m³/s
| System outdoor air method | ZoneSum
| Zone maximum outdoor air fraction | 1
| Cooling Supply Air Flow Rate Per Floor Area | 0.01 | m/s
| Cooling Fraction of Authosized Cooling Supply Air Flow Rate | 1
| Cooling Supply Air Flow Rate Per unit cooling capacity | 4e-05 | 1/Pa
| Heating Supply Air Flow Rate Per Floor Area | 0.01 | m/s
| Heating Fraction of Authosized Cooling Supply Air Flow Rate | 1
| Heating Fraction of Authorized Heating Supply Air Flow Rate | 1
| Heating Supply Air Flow Rate Per Unit Cooling Capacity | 3e-05 | 1/Pa
| Cooling Design Capacity Method | CoolingDesignCapacity
| Cooling Design Capacity | Autosized
| Cooling Design Capacity Per Floor Area | 234.7 | W/m²
| Fraction of Autosized Cooling Design Capacity | 1
| Heating Design Capacity Method | CoolingDesignCapacity
| Heating Design Capacity | Autosized
| Heating Design Capacity Per Floor Area | 157 | W/m²
| Fraction of Autosized Cooling Design Capacity | 1
| Central Cooling Capacity Control Method | OnOff
Coil cooling water | Availability schedule name | Always on, discret
| Design water flow rate | autosized | m³/s
| Design inlet water temperature | autosized | °C
| Design inlet air temperature | autosized | °C
| Design outlet air temperature | autosized | °C
| Design inlet air humidity ratio | autosized | kgH2O/kgair
| Design outlet humidity ratio | autosized | kgH2O/kgair
| Type of analysis | simple analysis
| Heat exchanger configuration | cross flow
Coil heating water | Availability schedule name | Always on, discret | -
| U-factor times area value | autosized | W/K
| Maximum water flow rate | autosized | m³/s
| Performance input method | Ufactor times area and design water flow rate | -
| Rated capacity | autosized | W/K
| Rated inlet water temperature | 49 | °C
| Rated inlet air temperature | 7.2 | °C
| Rated outlet water temperature | 38 | °C
| Rated outlet air temperature | 13 | °C
| Rated ratio for air and water convection | 0.5 | -
Fan Variable Volume | Fan total efficiency | 0.6572 | -
| Pressure rise | 995 | Pa
| Maximum flow rate | autosized | m³/s
| Fan power minimum flow rate input method | Fraction
| Fan power minimum fraction | 0.25
| Fan power minimum air flow rate | 0 | M³/s
| Motor efficiency | 0.954
| Motor in Airstream fraction | 1 | -
| Fan power coefficient 1 | 0.04076 | -
| Fan power coefficient 2 | 0.099
| Fan power coefficient 3 | -0.0729
| Fan power coefficient 4 | 0.9437
Setpoint manager, outdoor air reset | Control variable | Temperature | -
Air Terminal Single Duct VAV Reheat | Zone minimum air flw input method | constant | -
| Constant minimum air flow fraction | 0.2 | -
| Fixed minimum air flow rate | 0 | m³/s
| Maximum hot water or steam flow rate | 0 | m³/s
| Convergence tolerance | 0.001 | -
| Damper heating action | reverse with limit | -
| Maximum flow per zone floor area during reheat | autosized | -
| Maximum flow fraction during reheat | 0.5
| Maximum reheat air temperature | 40 | °C
Reheat coil, Heating, Water | Availability schedule | always on | -
| Performance input method | Ufactor x area and design water flow rate | -
| Rated capacity | autosized | - | 0.5
40
Thermal zones sizing: core, offices & hall | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | 15.5 | °C
| Dedicated outdoor air high setpoint temperature for design | 21 | °C
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -
Chilled water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 40 | °C
| Minimum loop temperature | 1 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 6.67 | °C
| Loop design temperature difference | 5.6 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Chiller electric, EIR | Reference capacity | autosized | W
| Reference COP | 5.33 | -
| Reference leaving chilled water temperature | 6.7 | °C
| Reference entering condenser fluid temperature | 35 | °C
| Reference chilled water flow rate | autosized | m³/s
| Reference condenser fluid flow rate | autosied | m³/s
| Minimum part load ratio | 0.15 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Minimum unloading ratio | 0.25 | -
| Condenser fan power ratio | 0 | -
| Fraction of compressor electric consumption rejected by condenser | 1 | -
| Leavind chilled water lower temperature limit | 2.3 | °C
Hot water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 10 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 50 | °C
| Loop design temperature difference | 11 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Boiler hot water | Fuel type | Natural gas | -
| Nominal capacity | autosized | W
| Nominal thermal efficiency | 0.933 | -
| Efficiency curve temperature evaluation variable | Leaving boiler | -
| Design water flow rate | autosized | m³/s
| Minimum part load ratio | 0 | -
| Maximum part load ratio | 1.2 | -
| Optimum part load ratio | 1 | -
| Water outlet upper temperature limit | 95 | °C
| Boiler flow mode | LeavingSetpointModulated | -
| Parasitic electric load | 0 | W
| Sizing factor | 1
Condenser water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 80 | °C
| Minimum loop temperature | 5 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 29.5 | °C
| Loop design temperature difference | 5.5 | K
| Sizing option | coincident
| Zone timesteps in averaging window | 6
Cooling tower, variable speed | Design inlet air wet-bulb temperature | 25.5 | °C
| Design approach temperature | 4 | K
| Design range temperature | 5.5 | K
| Design water flow rate | autosized | -
| Design air flow rate | autosized | -
| Design fan power | 63782 | W
| Minimum air flow rate ratio | 0.2 | -
| Fraction of tower capacity in free convection regime | 0.125 | -

## hvac_VRF
HVAC system, VRF: dedicated outdoor air system (DOAS) with variable refrigerant volume (VRF)
Two VAV systems | open plan offices, core, hall, 15 zones
data centers, 3 zones
VRF, variable refrigerant flow system with multiple indoor units and an outdoor unit |  |  |  |  | > | > | > | Systems
| Cooling type | DX cooling
| Heating type | electric heating
Time of operation | HVAC operation schedule | HVAC_Operation |  | see schedules
| Use night cycle | follow the hvac operation schedule | [5 empty] | - | ASHP | Air source heat pump
[11 empty] | definition | absorbs heat from a colder place and release it into a warmer place using the same vapor-compression refrigeration process and same external heat exchanger with fan as used by an air conditioners. Unlike an air conditioning unit, however, it is able to both warm and cool building
Supply air temperature | Supply air temperature schedule | Temperature setpoint schedule |  | see schedule
[8 empty] | x | EAHP | Exhaust Air Heat Pump
Mechanical ventilation | Economizer | no economizer | [8 empty] | definition | extracts heat from the exhaust air of a building and transfers the heat to the supply air, hot tap water and/or hydronic heating system (underfloor heating, radiators).
| Demand controlled ventilation | on
[8 empty] | x | GSHP | ground source heat pump
Availability managers | Applicability schedule | always on discrete |  | https://bigladdersoftware.com/epx/docs/8-9/input-output-reference/group-system-availability-managers.html
| Control type | Cycle on any | [5 empty] | v | VRF | Variable Refrigerant Flow
| Thermostat tolerance | 1 | K | [7 empty] | definition | use refrigerant as the cooling and heating medium. This refrigerant is conditioned by a single or multiple condensing units (which may be outdoors or indoors, water or air cooled), and is circulated within the building to multiple indoor units.
| Cycling run time control type | fixed run time
| Cycling run time | 3600 | s
Sizing system | Type of load to size on | Ventilation requirement
| Design outdoor air flow rate | autosized
| Central heating maximum system air flow ratio | 1
| Preheat design temperature | 7 | °C
| Preheat design humidity ratio | 0.008 | kgH2O/kgair
| Precool design temperature | 12.8 | °C
| Precool design humidity ratio | 0.008 | kgH2O/kgair
| Central cooling design supply air temperature | 12.5 | °C
| Central heating design supply air temperature | 21 | °C
| Sizing option | Coincident
| 100% outdoor air in cooling | yes
| 100% outdoor air in heating | yes
| Central cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Central heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | design day
| Cooling design air flow rate | 0 | m³/s
| Heating design air flow method | design day
| Heating design air flow rate | 0 | m³/s
| System outdoor air method | zone sum
| Zone maximum outdoor air fraction | 1
Coil Cooling DX Two Speed | Rated high speed total cooling capacity | autosized | W
| Rated high speed sensible heat ratio | autosized
| Rated high speed COP | 3
| Rated high speed air flow rate | autosized | m³/s
| Unit internal static air pressure | 773.3 | Pa
| Rated low speed total cooling capacity | autosized | W
| Rated low speed sensible heat ratio | 0.69
| Rated low speed COP | 3
| Rated low speed air flow rate | autosized | m³/s
| Minimum outdoor dry-bulb temperature for compressor operation | -25 | °C
Coil Heating DX Single Speed | Rated total heating capacity | autosized | W
| rated COP | 3.6
| Rated air flow rate | autosized | m³/s
| Unit internal static air pressure | 773.3 | Pa
| Minimum outdoor dry-bulb temperature for compressor operation | -8 | °C
| Maximum outdoor dry-bulb temperature for defrost operation | 5 | °C
Coil Heating, Electric | Availability schedule name | Always on, discret | -
| Efficiency | 1 | -
| Nominal capacity | autosized | -
Fan, Constant Volume | Fan total efficiency | 0.59 | -
| Pressure rise | 622 | Pa
| Maximum flow rate | autosized | m³/s
| Motor efficiency | 0.917 | -
Setpoint manager, outdoor air reset | Control variable | Temperature | -
| Setpoint at outdoor low temperature | 21 | °C
| Outdoor low temperature | 13 | °C
| Setpoint at outdoor high temperature | 15.5 | °C
| Outdoor high temperature | 21 | °C
Air Terminal Single Duct, Constant Volume, No Reheat | Maximum air flow rate | autosized | m³/s
Thermal zones sizing: core, offices & hall | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Zone heating sizing factor |  | -
| Zone cooling sizing factor |  | -
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | 15.5 | °C
| Dedicated outdoor air high setpoint temperature for design | 21 | °C
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -

## Thermal zones
Thermal zones
Cooling sizing parameters
For each zone | zone cooling design supply air temperature | 13 | °C
| zone cooling design supply air humidity ratio | 0.0085
zone cooling sizing factor
| cooling minimum air flow per zone floor area | 0.000762 | m³/s.m²
| Design zone air deistribution effectiveness in cooling mode | 1
| Cooling minimum air flow fraction | 0
| Cooling design air flow method | Design day
| Cooling design air flow rate | 0 | m³/s.m²
| Cooling minimum air flow | 0 | m³/s.m²
Heating sizing parameters
For each zone | zone heating design supply air temperature | 40 | °C
| zone heating design supply air humidity ratio | 0.008
zone heating sizing factor
| Heating maximum air flow per zone floor area | 0.002032 | m³/s.m²
| Design zone air distribution effectiveness in heating mode | 1
| Heating maximum air flow fraction | 0.3
| Heating design air flow method | Design day
| Heating design air flow rate | 0 | m³/s.m²
| Heating maximum air flow | 0.14158 | m³/s.m²

## Output Variables
Energy Plus, Output Variables
Weather
Site Outdoor Air Drybulb Temperature | Hourly
Equipment
Electric Equipment Electric Energy | Hourly
Lighting
Lights Electric Energy | Hourly
Zone Lights Electric Energy | Hourly
Internal gain
Zone Total Internal Total Heating Energy | Hourly
Comfort
Zone Air Temperature
Zone Mean Air Temperature | Hourly
Zone Mean Radiant Temperature | Hourly
Zone Operative Temperature | Hourly
Zone Thermal Comfort CEN 15251 Adaptive Model Temperature | Hourly
Zone Thermal Comfort ASHRAE55 Adaptive Model Temperature | Hourly
Ventilation
Zone Ventilation Fan Electric Energy | Hourly
Windows
Zone Windows Total Heat Gain Energy | Hourly
Zone Windows Total Heat Loss Energy | Hourly
Zone Windows Total Transmitted Solar Radiation Rate | Hourly
Zone Windows Total Transmitted Solar Radiation Energy | Hourly

## Simulations
Scenario analysis, glazing types
48 | 3 steps, 16 runs each | a | b | c
| step # | 1 | 2 | 3
| name | glazing type | int shading | ext shading
| number of simulations | 16 | 16 | 16
| exterior shading | no | no | yes
| interior shading | no | yes | no
| interior thermal curtain | no | no | no
main parameters
| cooling setpoint | 26
| heating setpoint | 21
| HVAC | fan coil, basic
| electricity grid | BE
| density, offices | 8 m²/p.
| lighting power | 8 W/m²
| types of glazing | 16, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
single glazing, w/ frame low-perf
single glazing, coated, w/ frame low-perf
double glazing, coated, 6 types, w/ frame high-perf
triple glazing, coated, 6 types, w/ frame high-perf
Sensitivity analysis, hvac system
64 | 4 steps, 16 runs each | d | e | f | g
| step # | 4 | 5 | 6 | 7
| name | VAV+, 26-21 | VAV+, 26-21 | VRF, 26-21 | VRF, 26-21
| number of simulations | 16 | 16 | 16 | 16
| HVAC | VAV, efficient | VAV, efficient | VRF | VRF
| exterior shading | no | no | no | no
| interior shading | no | yes | no | yes
| cooling setpoint | 26 | 26 | 26 | 26
| heating setpoint | 21 | 21 | 21 | 21
main parameters
| electricity grid | BE
| density, offices | 8 m²/p.
| lighting power | 8 W/m²
| types of glazing | 16, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
single glazing, w/ frame low-perf
single glazing, coated, w/ frame low-perf
double glazing, coated, 6 types, w/ frame high-perf
triple glazing, coated, 6 types, w/ frame high-perf
Scenario analysis, glass-to-wall ratio
8 | 1 steps, 8 runs | h
| step # | 8
| name | glazing type
| number of simulations | 8
| glass-to-wall ratio | 75% of the width
main parameters
| cooling setpoint | 26
| heating setpoint | 21
| HVAC | VAV, efficient
| electricity grid | BE
| density, offices | 8 m²/p.
| lighting power | 8 W/m²
| exterior shading | no
| interior shading | no
| types of glazing | 8, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
double glazing, coated, 3 types, w/ frame high-perf
triple glazing, coated, 3 types, w/ frame high-perf
Scenario analysis, high-tech
9 | 7 steps, 1 run each except DSF | i | i | i | i | i | i | i
| step # | 9 | 9 | 9 | 9 | 9 | 9 | 9
| name | krypton, dg | krypton, tg | xenon, tg | CCF | vaccum | smart | DSF
| number of simulations | 1 | 1 | 1 | 1 | 1 | 1 | 3
| types of glazing | double glazing, krypton | triple glazing, krypton | triple glazing, xenon | closed cavity facade | vaccum glazing | smart double glazing | DSF, min, mean, max
No BEM for DSF, see note
main parameters
| cooling setpoint | 26
| heating setpoint | 21
| HVAC | VAV, efficient
| electricity grid | BE
| density, offices | 8 m²/p.
| lighting power | 8 W/m²
| exterior shading | no
| interior shading | yes | except for smart glazing. For CCF and DSF: between glass panes
Sensitivity analysis, setpoint temperature
16 | 2 steps, 8 runs each | j | k
| step # | 10 | 11
| name | americanisation | sufficiency
| number of simulations | 8 | 8
| cooling setpoint | 24 | 27
| heating setpoint | 21 | 19
| exterior shading | no | yes
| interior shading | no | no
main parameters
| HVAC | VAV, efficient
| electricity grid | BE
| density, offices | 8 m²/p.
| lighting power | 8 W/m²
| types of glazing | 8, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
double glazing, coated, 3 types, w/ frame high-perf
triple glazing, coated, 3 types, w/ frame high-perf
Sensitivity analysis, internal gains
16 | 2 steps, 8 runs each | l | m
| step # | 12 | 13
| name | density_6 | density_10
| number of simulations | 8 | 8
| lighting power | 10 W/m² | 5 W/m²
| density, offices | 6.5 m²/p. | 10 m²/p.
main parameters
| cooling setpoint | 26
| heating setpoint | 21
| HVAC | VAV, efficient
| electricity grid | BE
| exterior shading | no
| interior shading | yes
| types of glazing | 8, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
double glazing, coated, 3 types, w/ frame high-perf
triple glazing, coated, 3 types, w/ frame high-perf
Sensitivity analysis, climate change
48 | 3 step, 2 x 8 runs each | n-o | p-q | r-s
| step # | 14-15 | 16-17 | 18-19
| name | climate change | climate change | climate change
| number of simulations | 8 | 8 | 8
| exterior shading | no | no | yes
| interior shading | yes | no | no
| cooling setpoint | 26 | 24 | 27
| heating setpoint | 21 | 21 | 19
| weather data | HadCM3-A2 2050 / 2080 | HadCM3-A2 2050 / 2080 | HadCM3-A2 2050 / 2080
main parameters
| HVAC | VAV, efficient
| electricity grid | BE
| lighting power | 8 W/m²
| density, offices | 8 m²/p.
| types of glazing | 8, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
double glazing, coated, 3 types, w/ frame high-perf
triple glazing, coated, 3 types, w/ frame high-perf
Sensitivity analysis, energy mix for electricity from grid
LCA ONLY
40 | 5 steps, 8 runs each | q | r | s | t | u | v
| step | 25 | 26 | 27 | 28 | 29 | 30
| name | NL | DE | PL | FR | CH | DK
| number of simulations | 8 | 8 | 8 | 8 | 8 | 9
| electricity grid | Netherlands | Germany | Poland | France | Switzerland | Denmark
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| lighting power | 8 W/m²
| density, offices | 8 m²/p.
| exterior shading | yes
| interior thermal curtain | no
| types of glazing | 8, which are:
init: old double glazing, bronze, w/ frame low-perf
double glazing, clear, air, w/ frame low-perf
double glazing, coated, 3 types, w/ frame high-perf
triple glazing, coated, 3 types, w/ frame high-perf
Note on I91: The analysis of the double skin facade system is not based on energy modelling, but on the results of a review conducted by Pomponi et al. on more than 50 publications. Pomponi et al., 2016. "Energy performance of Double-Skin Façades in temperate climates: A systematic review and meta-analysis," Renewable and Sustainable Energy Reviews. The authors summarise the results in terms of possible energy use reduction. The average reduction in heating load is 33%, but with a high degree of variability. Taking into account the 75th and 25th percentiles, the maximum reduction is about 50% and the minimum about 20%. The average reduction of the cooling load is 28%, with slightly less variability than in the case of the heating load. Taking into account the 75th and 25th percentiles, the maximum reduction is 40% and the minimum 20%. These values are applied to the average energy use for double and triple glazing with exterior shading device (step2)

## LCA
LCA
Software
Brightway2 | https://brightway.dev/
Main database
Ecoinvent | https://ecoinvent.org/
Own one | Defined in Excel
System model
cut-off system model | https://ecoinvent.org/the-ecoinvent-database/system-models/
Updated LCI, including regionalisation
aluminium, wrought alloy, production | RER
market for aluminium, wrought alloy | RER
flat glass production, uncoated | BE
flat glass production, coated | BE
tempered safety glass production | BE
laminated safety glass production | BE
New LCI
smart glass production | BE
IGUs production | BE
aluminium frame production, low or high performance, for single, double or triple glazing | BE
thermal curtain production, sheep wool, metallised | BE
screen production, metalised blind fabric | BE
curtain walls production | BE

## hyp_frames
Variables and parameters
symbol | unit | comments
H_cw | m | Height of a glazed unit of curtain wall
w_cw | m | Width of a glazed unit of curtain wall
H_glass | m | Height of the glazed part of the curtain wall, including frame width
w_glass | m | Width of the glazed part of the curtain wall, including frame width
w_frame | m | Width of the frame
S_glass | m² | Total area of the IGU
m_alu | kg | total mass of aluminium per linear meter of frame
m_epdm | kg | total mass of EPDM per linear meter of frame
m_wood | kg | total mass of wood in low performance frame
L_frame | m | Total length of frame
Constant, per unit of glazed section of curtain wall
symbol | value | unit | comments
H_cw | 2.35 | m
w_cw | 1.5 | m
w_frame | 0.05 | m
S_cw | 3.525 | m²
H_glass | 2.3 | m
w_glass | 1.45 | m
S_glass | 3.335 | m²
L_frame | 7.7 | m
Constant, per m² of glazed section of curtain wall
symbol | value | unit | comments
S_glass | 0.9461 | m² | Surface of glass per m² of glazed curtain wall
L_frame | 2.1844 | m² | Length of alu frame per m² of glazed curtain wall
Frame_Low performance_SG, per linear meter of frame
symbol | value | unit | comments
m_alu | 3.3116 | kg
m_wood | 0.00015 | m³
m_wood | 0.09 | kg
Frame_High performance_SG, per linear meter of frame
symbol | value | unit | comments
m_alu | 3.3116 | kg
m_epdm | 0.05475 | kg
Frame_Low performance_DG, per linear meter of frame
symbol | value | unit | comments
m_alu | 3.4749 | kg
m_wood | 0.00015 | m³
m_wood | 0.09 | kg
Frame_High performance_DG, per linear meter of frame
symbol | value | unit | comments
m_alu | 3.4749 | kg
m_epdm | 0.0675 | kg
Frame_High performance_TG, per linear meter of frame
symbol | value | unit | comments
m_alu | 3.7868 | kg
m_epdm | 0.078 | kg

## hyp_igus
Overall parameters
param | unit | value | formula | comments
g_density | t/m³ | 2.5 |  | glass density
g_area | millimeter | 1 |  | area of glass sheet
t_tsg | millimeter | 10 |  | thickness of the tempered safety glass
t_lsg | millimeter | 10 |  | thickness of the laminated safety glass
n_pvb | unit | 2 |  | number of PVB layers for LSG
m_dg | kilogram |  | g_density * (t_lsg * (lsg_uncoated_area + lsg_coated_area) + g_uncoated_thickness + g_coated_thickness) + 0.6 * n_spacer | total mass of the igu
m_tg | kilogram |  | g_density * (t_lsg * (lsg_uncoated_area + lsg_coated_area) + g_uncoated_thickness + g_coated_thickness) + 0.6 * n_spacer | total mass of the igu
m_smartg | kilogram |  | g_density * (t_lsg * (lsg_uncoated_area + lsg_coated_area) + g_uncoated_thickness + g_coated_thickness) + 0.6 * n_spacer | total mass of the igu
waste_coeff | unit | -1 |  | negative flows for waste generation
d1 | kilometer | 125 |  | distance btw the IGU processing plant and the construction site
t_g_ext | millimeter | 8 |  | thickness of the exterior glass sheet
t_g_mid_tg | millimeter | 6 |  | thickness of the intermediate glass sheet for triple glazing
t_g_uncoated_int | millimeter | 8 |  | thickness of the interior glass sheet for igu w/o lsg

## Questions
|  |  | SG | 77 |  | 66 | 30/20
|  |  | DG opt | 20 |  | 35
GvM |  | w/dg_init | HVAC Elec, MJ/m² | kWh | HVAC gas, MJ/m² | kWh
VAV | _init |  | 149.1 | 41.4167 | 95.7 | 26.5833
VAV | Variable Air Volume (VAV) chiller with gas boiler reheat |  | 206 | 57.2222 | 110 | 30.5556
| Variable Air Volume (VAV) air-cooled chiller with gas boiler reheat |  | 250 | 69.4444
DOAS | Dedicated outdoor air system (DOAS) with fan coil chiller with boiler |  | 282 | 78.3333 | 180 | 50 | test variable air volume
| Dedicated outdoor air system (DOAS) with fan coil air-cooled chiller with boiler |  | 153 | 42.5 | 180 | 50
| Dedicated outdoor air system (DOAS) with radiant slab air-cooled chiller with boiler |  | 280 | 77.7778 | 347 | 96.3889
DOAS + heat pump | Dedicated outdoor air system (DOAS) with fan coil chiller with central air source heat pump
Dedicated outdoor air system (DOAS) with fan coil air-cooled chiller with central air source heat pump
Dedicated outdoor air system (DOAS) with radiant slab chiller with central air source heat pump
Dedicated outdoor air system (DOAS) with radiant slab air-cooled chiller with central air source heat pump
Dedicated outdoor air system (DOAS) with water source heat pumps cooling tower with boiler
Dedicated outdoor air system (DOAS) with water source heat pumps with ground source heat pump
DOAS + VRF | Dedicated outdoor air system (DOAS) with variable refrigerant volume (VRF) |  | 162 | 45 |  | 0
VRF | variable refrigerant volume (VRF) |  | 134 | 37.2222 |  | 0
VAV + heat pump | Variable Air Volume (VAV) chiller with central air source heat pump reheat
Variable Air Volume (VAV) air-cooled chiller with central air source heat pump reheat
PVAV | Packaged Variable Air Volume (PVAV) with gas boiler reheat
PVAV + heat pump | Packaged Variable Air Volume (PVAV) with central air source heat pump reheat
Heat pump | Water source heat pumps cooling tower with boiler
Water source heat pumps with ground source heat pump
Fan coil | Fan coil chiller with boiler
Fan coil chiller with central air source heat pump
Fan coil air-cooled chiller with boiler
Fan coil air-cooled chiller with central air source heat pump